IP-PDU Firmware patches Instruction

- Overview:

To solve the IP-PDU system crash problem by the J-LINK and two .hex files.

2. Details:

  - Preparation

2.1.1 Please prepare one J-LINK debug probes with 5 pin(See below Figure 1) and one computer/laptop;

Figure 1

2.1.2. Install the J-LINK driver (please ignore this if the driver was installed already in your PC/Loptop). Click the Start to see if you can see the SEGGER file as figure 2

Figure 2

3. Configuration before upload program

3.1 Please disassembly the IP-PDU module, connect the 5pin module of J-LINK to the IP-PDU module. Please make sure the PIN connect to the corresponding TMS, TCK, NRST, GND, 3.3V from the top to bottom as figure 3.

Figure 3

2.2、3. 2 Open up Start -> All programs,  find SEGGER and click J-Flash as figure 4.

Figure 4

3.3 You will get below Figure 5 after point 3.2

Figure 5

3.3.1 Click Option —> Project setting… to do the setting as figure 6

Figure 6

3.3.2 Click Target Interface as figure 7

图7

3.3.3. Click CUP and select ST STM32F407VG by click icon  as figure 8

Figure 8

3.3.4. Click Production and tick Erase/ Program/ Verify/ Start application, then click OK as figure 9.

Note: Please do NOT tick Secure chip checkbox!

图9

4. Uplaod the .hex files

4.1 Click File —>Open data file… and select the .hex file(First_IPv1_IAP.hex）, then press F7 from your PC/Laptop to upload the file. You can view the status by the program bar. Close the dialog box if upload finished. See figure 10 as below:

Figure 10

3.2、4.2 Click File —>Open data file… and select the .hex file(Second_IPv1_IAP.hex）, then press F7 from your PC/Laptop to upload the file. You can view the status by the program bar. Close the dialog box if upload finished. See figure 11 as below:

Figure 11

That’s all for the firmware patches instruction. If everything is fine, the IP-PDU module will come back to again.