NetmateⅡ Mini

Web-based SNMP Card for UPS

User’s Manual

Content

Chapter 1 Introduction	4

1.1	Introduction	4

1.2	Features	4

1.3	Function	5

Chapter 2 Installation Requirement	5

Chapter 3 Topologies	6

Chapter 4 Appearance and Installation	7

4.1 Appearance	7

4.2 Components	9

4.3 Installation	10

Chapter 5 Web Configuration	10

5.1 Login via Web browser	10

5.2 Web Operation Introduction	11

5.2.1 Status Inquiry	11

5.2.1.1 System Basic Information	12

5.2.1.2 Bus Device Information	14

5.2.1.3 Device Basic Information	15

5.2.1.4 Current Run Status	17

5.2.2 Parameter Settings	18

5.2.2.1 System Setting	19

5.2.2.2 485 Bus Device Settings	21

5.2.2.3 Network Settings	22

5.2.2.4 SNMP Settings	24

5.2.2.5 Warning Settings	25

5.2.2.6 User Settings	28

5.2.2.7 System Time Settings	29

5.2.3 Remote Control	30

5.2.3.1 Instant Control	30

5.2.3.2 Task Scheduler	31

5.2.3.3 Extend Output Control	32

5.2.3.4 Netmate Update	32

5.2.4 History Record	32

5.2.4.1 History Event Record	32

5.2.4.2 History Data Maintenance	33

5.2.5 System Help	33

5.2.5.1 System Help	33

5.2.5.2 About Netmate	34

Chapter 6 Common Problem Solutions	34

6.1 Forget the IP address, how to do?	34

6.2 why the device can be PING, but user can not open the page?	35

6.3 What is the login user name and password?	40

6.4 Forget the login password, how to do?	41

6.5 Cannot connect with the device, how to do?	41

Chapter 7 Notice Items	41

# Chapter 1 Introduction

## Introduction

Netmate II Mini UPS network monitor adapter card is a new standard UPS network centralized monitoring products with delicate design. The function includes Email and SMS warning, task schedule, history event and history data record, etc. Its graphical interface is easy to operate with mature and stable hardware platform, and able to extend various devices through RS422 port (RJ45 form), such as temperature and humidity module, 4i2o signal collecting module, remote power control module, air conditioning infrared module, battery power module, sensors (smoke sensor, water leakage sensor, door contact, sound-light alarm), etc.

## Features

- Network mode: LAN based on IP, Wan, Internet, ADSL, E1, wireless Ethernet, etc;

- Provide the safe and reliable user authority management;

- Built-in optimal IP Power communication protocol, guarantee the real-time data acquisition and make full use of bandwidth;

- Support many configuration management modes such as Telnet, Hyper Terminal, Web browser;

- Support task schedule, UPS timing open/shutdown setting, battery timing discharge, etc;

- Compatible with different brands and types of UPS;

- Support history data and history event record;

- Built-in system clock supports automatic reset to achieve time synchronization;

- Support many network protocols such as SNMP, HTTP, DNS, SMTP, SNTP DHCP, etc;

- Support to extend 2 channels of temperature and humidity module;

- Support Email alarm;

- Match with SMS alarm service to achieve alarm function.

## Function

- Remote monitoring for UPS through network;

- User interface based on Web;

- Compatible with multi-brand and multi-type of UPS;

- Support SMS alarm;

- Support Email alarm;

- Multi-user authority management;

- Support DHCP;

- Support remote self-test, shutdown and restart UPS function (Required UPS support);

- Configuration via Telnet, Hyper Terminal and Webpage;

- Task schedule (timing self-test, open / shutdown);

- Record history event and history data;

- Remote monitoring and managing for UPS through HTTP, SNMP, Java applet, Telnet and IP Power software;

- Ability to extend temperature and humidity module;

- Match with IP Power software to achieve centralized monitoring and unified management;

- Match with IP Power software to achieve shutdown protection for client-end.

# Chapter 2 Installation Requirement

- A smart UPS with RS-232 communication port;

- A computer with RS-232 serial port and 10M/100M Ethernet adapter for initial configuration;

- An available physical connection to an existing network;

- A complete network environment;

- Function extension equipment, which is used for network monitoring & managing UPS, computer room environment devices (optional).

# Chapter 3 Topologies

# Chapter 4 Appearance and Installation

## 4.1 Appearance

External

Internal

- P: Power indicator (green), constantly on;

- R: Running indicator (red), slow flash shows normal working, constantly on or no flash shows the program NOT running or the system halted;

- E: UPS communication indicator (green), constantly on shows device is connected with UPS communication, flash shows the device is disconnected with UPS communication;

- RS232 Port: when using hyper terminal to configure, we need to use white configuration cable RS-232 and PS2 →RS232 port cable to connect;

- RS422: to extend other devices;

- LAN: Interface of UTP 10/100M RJ45 Ethernet.

## 4.2 Components

| Netmate II Mini（Internal） | 1 Netmate II Mini card, 1 PS2→RS232 port cable, 1 white configuration cable, 1 IP Power SE CD (including instruction, installation procedure, etc), 1 guarantee card, 1 certificate. |
| --- | --- |
| Netmate II Mini（External） | 1 Netmate II Mini adapter, 1 PS2→RS232 port cable, 1 white configuration cable, 1 IP Power SE CD (including instruction, installation procedure, etc), 1 guarantee card, 1 certificate, 1 power adapter. |

## 4.3 Installation

Internal: insert the Netmate Ⅱ Mini internal card to the slot of UPS, and connect it to network via Ethernet port.

External: connect the Netmate Ⅱ Mini to network via Ethernet port; connect the white configuration cable RS-232 from it to the RS232 port of UPS.

# Chapter 5 Web Configuration

## 5.1 Login via Web Browser

Netmate Ⅱ Mini supports HTTP network protocol so that users can login to operate easily via Web browser such as Microsoft Internet Explorer and Netscape. Here we take IE for example.

  - Open an IE browser;

  - Enter the Netmate Ⅱ Mini IP address (default IP address is 192.168.0.100), the system will display the following interface;

（Users can change the IP according to their own network environment.）

3）Enter User name and Password in the box, its default User and Password are both “admin”.

（Users can change the User name and Password.）

5.2 Web Operation

Enter the main function item，the sub-menu items will be shown on the left side of the page. When using this Netmate Ⅱ Mini for the first time，please enter the [Parameter Settings] menu item to set all the configuration items, and then the UPS status could be correctly displayed by other pages.

Enter Netmate Ⅱ Mini UPS Webpage，there are 5 main function items in the first Web page：

- Status Inquiry

- Parameter Settings

- Remote Control

- History Record

- System Help

Netmate Ⅱ Mini Main Function Item

### 5.2.1 Status Inquiry

Sub-Menu：

- System Basic Information

- Bus Device Information

- Device Basic Information

- Current Running Status

#### 5.2.1.1 System Basic Information

This page is to display system basic information and network information. Values shown here are either providing by Netmate Ⅱ Mini itself or they are user settings from the [Parameter Settings] page.

1. Basic Information

This part is to display basic information. Values in System Name/System Administrator/System Installation Position/Hardware Version/Software Version Product Serial Number are provided by Netmate Ⅱ Mini itself, other values come from user’s settings in [Parameter Settings] page.

  - System Name

This part will display the information automatically when users have finished the settings in [SNMP Settings] page.

  - System Administrator

This part will display the information automatically when users have finished the settings in [SNMP Settings] page.

  - System Installation Position

This part will display the information automatically when users have finished the settings in [SNMP Settings] page.

  - System Current Time

Current Time of Netmate Ⅱ Mini，it will be refreshed according to users' settings in [System Time Settings] page.

  - System Run Time

Current Run Time of Netmate Ⅱ Mini.

  - Other information is provided by Netmate Ⅱ Mini system itself.

2. Network Information

This part is to display network information. The MAC address is provided by Netmate Ⅱ Mini. All other values in this section come from your settings in [Parameter Settings] page.

A, IP Address

This part will display the information automatically when users have finished the settings in [Network Settings] page.

B, Subnet Mask

This part will display the information automatically when users have finished the settings in [Network Settings] page.

C, Gateway

This part will display the information automatically when users have finished the settings in [Network Settings] page.

D, Primary DNS Server

This part will display the information automatically when users have finished the settings in [Network Settings] page.

E, Secondary DNS Server

This part will display the information automatically when users have finished the settings in [Network Settings] page.

F, Primary Time Server

This part will display the information automatically when users have finished the settings in [System Time Settings] page.

G, Secondary Time Server

This part will display the information automatically when users have finished the settings in [System Time Settings] page.

H, SMTP Server

This part will display the information automatically when users have finished the settings in [Warning Settings] page.

I, MAC Address

The information is provided by Netmate Ⅱ Mini system automatically.

#### 5.2.1.2 Bus Device Information

This page is to display analog data status of the signal collection card and environment status, which can be realized by connecting with relevant modules such as signal collection module, temperature and humidity module, etc.

1. Signal Collect Card Analog Data Status and Signal Collect Card Switch Data Status

Need to connect with signal collection module, after connection, users can set the parameters in [485 Bus Device Settings] page.

2. Environment Status (total 2 Bus)

Need to connect with temperature and humidity module, after connection, users can set the parameters in [System Settings] page.

#### 5.2.1.3 Device Basic Information

This part is to display basic information of each part of the device (UPS Basic Information, Battery Information, Rating Information and Warning Definition Information. The content will change according to users’ settings and UPS real situation.

1. Basic Information

Information about UPS Manufacturer/Model/Type/Version/Current System Time is provided by the UPS automatically.

2. Battery Information

Values here are current battery information of UPS.

A, Battery Number

Display the battery number of the UPS. This part will display the information automatically when users have finished the settings in [System Settings] page.

B, Battery Charge Voltage

Display the battery Charge Voltage. This part will display the information automatically when users have finished the settings in [System Settings] page.

C, The Latest Battery Change Time

Display the latest battery change time. This part will display the information automatically when users have finished the settings in [System Settings] page.

D, Battery Used Time

Display battery used time, the information will be provided by Netmate Ⅱ Mini automatically.

3. Rating Information

Values here are all provided by the UPS automatically.

4. Warning Definition Information

This part will display the information automatically when users have finished the settings in [System Settings] page.

A, Offline Inquiry Time

Display the inquiry time interval whether UPS is offline. This part will display the information automatically when users have finished the settings in [System Settings] page.

B, Offline Inquiry Times

Display the inquiry times whether UPS is offline. This part will display the information automatically when users have finished the settings in [System Settings] page.

C, Input Voltage Upper Limit

Display the input voltage upper limit of UPS. This part will display the information automatically when users have finished the settings in [System Settings] page.

D, Input Voltage Lower Limit

Display the input voltage lower limit of UPS. This part will display the information automatically when users have finished the settings in [System Settings] page.

E, Load Upper Limit

Display the added load upper limit values. This part will display the information automatically when users have finished the settings in [System Settings] page.

F, Temperature Upper Limit

Display the temperature upper limit values. This part will display the information automatically when users have finished the settings in [System Settings] page.

G, Battery Low Electric Level

Display the battery low electric level values. This part will display the information automatically when users have finished the settings in [System Settings] page.

H, Battery Life

Display the battery life values. This part will display the information automatically when users have finished the settings in [System Settings] page.

#### 5.2.1.4 Current Running Status

This part is to display the current UPS all kinds of running status values and running status chart. You can check the current running status of the UPS clearly，when an abnormal status condition happens, values here will be shown in red (single-phase).

Single-phase UPS Running Page

Three-phase UPS Running Page

Basic Information

The current values about Input Voltage/Input frequency/Battery Voltage/Battery Content/UPS Temperature/Environment Temperature/ Environment Humidity/Output Voltage/Output Max Voltage/Output Min Voltage/ Current Load are displayed here.

Current Running Status

The current running status about connection/AC/Switch/UPS/Working /Battery/Testing/Beep is displayed here.

### 5.2.2 Parameter Settings

Sub-Menu:

- System Settings

- 485 Bus Device Settings

- Network Settings

- Warning Settings

- User Settings

- System Time Settings

#### 5.2.2.1 System Settings

This page is to set UPS basic parameter, warning definition, UPS warning and switch off setting, it can also add or revise UPS load device.

1. Basic Parameter Settings

This part is to set up the UPS basic parameter. The communication protocol is default, Baud Rate/ Battery Type/ Battery Charge Voltage/Latest Battery Change Time need to be set according to users UPS real situation. (Please refer to the UPS manual)

2. Warning Definition Settings

A, Inquiry Time

Set the inquiry interval time to check whether UPS is offline.

B, Offline Times

Set the inquiry times to check whether UPS is offline. If UPS status is always offline during the inquiry times, the system will judge the UPS offline and send warning.

C, Input Voltage Upper Limit

Set current voltage upper limit, if the UPS input voltage exceeds the upper limit value, the system will send the warning.

D, Input Voltage Lower Limit

Set current voltage lower limit, if the UPS input voltage is lower than the Lower limit value, the system will send warning.

E, UPS Load Upper Limit

Set current load upper limit, if the UPS load exceeds the upper limit value, the system will send warning.

F, UPS Battery Low Electric Level

Set current UPS battery voltage lower limit, if the UPS battery voltage is lower than the lower limit value, the system will send warning.

G, UPS Temperature Upper Limit

Set current UPS temperature upper limit, if the UPS temperature exceeds the upper limit value, the system will send warning.

H, UPS Battery Life

Set current UPS battery life，if the UPS battery used time exceeds the Battery Life, the system will send warning.

3. UPS Warning, Switch Off Settings

This part is to set whether send Warning and Switch Off message when the UPS is abnormal. This part can also set the Switch Off Delay Time after sending warning message and before the Switch Off starts.

4. Load Device List

This part can list the server’s name and IP; it is convenient for user to manage.

#### 5.2.2.2 485 Bus Device Settings

This page is to set up the signal collect card parameters. It needs to connect signal collect module and enable the bus collect card in [system settings] page, which support 4 channels dry contact signal input and 2 channels output control.

1.485 Bus Device Configuration Parameter

This part is to set up Inquiry Time Interval/Offline Times/Respond Await Time/Temperature and Humidity module Numbers of 485 Bus Device; it can also enable the Bus Collect Card.

A, Inquiry Time Interval

Set inquiry time interval to check whether the device is offline.

B, Offline Times

Set inquiry offline times to check whether the bus device is offline. If bus device is offline all the time during the set inquiry times, the system will judge the bus device offline and send warning.

C, Respond Await Time

Set respond await time.

D, Enable Bus Collect Card

Set in order to start the bus collect card.

E, Temperature and Humidity Module Number

Set temperature and humidity module extending number.

2. Temperature and Humidity Alarm Settings

This part is to set up the Upper and Lower limit of temperature and humidity, it can also set up the tolerance numerical value of temperature and humidity. It will send warning messages when the temperature and humidity of UPS exceeds the limit. (This part needs to connect the temperature and humidity module)

A, Alarm Description

Set alarm description, it is convenient for users to distinguish the alarm position.

B, Temperature Alarm Upper Limit

Set current temperature alarm upper limit, if the UPS temperature exceeds the upper limit value, the system will send warning.

C, Temperature Alarm Lower Limit

Set current UPS temperature alarm lower limit, if the UPS temperature is lower than the lower limit value, the system will send warning.

D, Temperature Tolerance Numerical Value

Set temperature tolerance numerical value.

E, Humidity Alarm Upper Limit

Set current humidity alarm upper limit, if the humidity exceeds the upper limit value, the system will send warning.

F, Humidity Alarm Lower Limit

Set current humidity alarm lower limit, if the humidity is lower than the lower limit value, the system will send warning.

G, Humidity Tolerance Numerical Value

Set humidity tolerance numerical value.

#### 5.2.2.3 Network Settings

This page is to set Basic Network Settings/DNS Server Settings/Enable Options, which is used to communicate with UPS via network.

1. Basic Network Settings

A, IP Access Method

When choosing DHCP Auto Access, IP address/Subnet Mark/Gateway items will turn gray, user cannot modify it. When choosing Manual Setting, user can modify it.

B, Other Items

The MAC Address is provided by Netmate Ⅱ Mini, user can not reset it. Users can set the IP Address, Subnet Mark, and Gateway freely according to real situation, but the IP Address should not be conflicted with other IP.

2. DNS Server Settings

User can set the Primary DNS Server and Secondary DNS Server IP address, when the Primary Server can not work normally, the system will choose the Secondary DNS Server IP address.

3. Enable Options

User can set the Enable Options, including Enable SNMP/ Enable GSM/ Enable TELNET/ Enable HTTP/ Enable IPPOWER.

A, Enable SNMP

Choose whether enable SNMP (Simple Network Management Protocol）, that is to say, users can choose whether allow users to monitor and manage UPS via SNMP Network Management software.

B, Enable GSM

Choose whether enable GSM, that is to say, users can choose whether allow users to monitor and manage UPS via GSM.

C, Enable TELNET

Choose whether enable TELNET, that is to say, users can choose whether allow users to remote login Netmate Ⅱ Mini Web Server via TELNET. After choosing Enable TELNET, users still need to set the needed port number of Netmate Ⅱ Mini Web Server via TELNET.

D, Enable HTTP

Choose whether enable HTTP, that is to say, users can choose whether allow users to login Netmate Ⅱ Mini Web Server via Web browser. After choosing Enable TELNET, users still need to set the needed port number of Netmate Ⅱ Mini Web Server via Web browser.

E, Enable IPPOWER

Choose whether enable IPPOWER, that is to say, users can choose whether allow users to monitor and manage UPS via IPPOWER software. After choosing Enable IPPOWER, users still need to set the needed communication password of IPPOWER software and Netmate Ⅱ Mini.

#### 5.2.2.4 SNMP Settings

This page is to set the relevant needed settings, when the Netmate Ⅱ Mini is matched with SNMP software, including Basic Settings, Authorization Settings and TRAP Settings.

1. Basic Settings

A, System Name

Name the Netmate Ⅱ Mini.

B, System Administrator

Set the administrator of the Netmate Ⅱ Mini.

C, System Installation Position

Set Netmate Ⅱ Mini installation location.

(The Basic Settings is convenient for centralized monitoring and management, when using many devices. Users can inquire each device fast and simply)

2. Authorization Settings

This part is to set SNMP users’ IP Address, Community and relevant Authorization. Users can set 10 SNMP users IP Address at most, and can choose the Authorization which includes No Authorization, Readable and Readable/Writable.

3. Trap Settings

Receiver IP Address is used to receive traps sent by Netmate Ⅱ Mini. Users can set 4 Trap Receivers IP address at most. Users can also choose whether receive the traps.

#### 5.2.2.5 Warning Settings

This page is to set the relevant configuration by Email and Mobile SMS alarm. It includes Email Settings, Receiver Settings, Mobile Information Configuration and Mobile Receiver Settings.

1. Email Settings

SMTP Server: This section is to set the IP Address/ Port/ Sender Mailbox of Netmate Ⅱ Mini Email Server. If the SMTP Server needs to authorize, users need to set Email user name and password. Note that free email server such as Hotmail, Yahoo are not allowed.

2. Receiver settings

This part is to set Mailbox to receive Email warning and log when an event occurs. Users can set 8 Email addresses at most.

Click the “Select” button of Warning Event, the system will pop out the following box, users can choose the needed events to receive by Email. Users can also choose whether send warning and log.

3. Mobile Information Configuration

This part is to show the interface of another product ——MobileMate， with the following function which Netmate Ⅱ Mini does not include.

Local GSM Modem

Users need to choose to send warning or log via Local GSM Modem in Device in Use part, then set the GSM Modem Baud Rate, Mobile SMS Center Number, Warning time interval, Warning times and UPS running status sending time interval.

4. Mobile Receiver Setting

This part is to show the interface of MobileMate with the following function which Netmate Ⅱ Mini does not include.

Send warning or log via Local GSM Modem

This part is to set Mobile Number to receive Warning Event sent by Netmate Ⅱ Mini when an event occurs. Users can set 6 mobile numbers at most.

Click the “Select” button of Warning Event，the system will pop out the following box, users can choose the needed events to receive by Email. Users can also choose whether send warning and log.

#### 5.2.2.6 User Settings

This page is to set the user information which is used to login Netmate Ⅱ Mini via Web or Telnet, and manage its user information via IP Power software.

1. Web/Telnet User Settings

This part is to set Web/Telnet User Authorization. Users have the authorization to access, control or manage the system.

2. IP POWER User Settings

This part is to set the authorized IP　address, all the authorized address can be managed via IP Power software. Authorization item includes Manage and Access.

#### 5.2.2.7 System Time Settings

This page is to update the current system time of Netmate Ⅱ Mini. It provides two kinds of update ways, Manual Reset and Auto Reset.

1. System Current Time

Display current system time of Netmate Ⅱ Mini, it is provided by Netmate Ⅱ Mini automatically, and will change according to user’s settings.

2. Manual Reset

Set current system time.

3. Auto Reset

A, Primary Time Server

Set current primary time server IP address of Netmate Ⅱ Mini.

B, Secondary Time server

Set current secondary time server IP address of Netmate Ⅱ Mini， when the primary time server cannot work normally, the system will choose secondary time server to proofreading time automatically.

C, Auto Refresh Time Interval

Set auto refresh time interval of current Netmate Ⅱ Mini system time.

D, Instant Refresh

Choose whether refresh the current system time of Netmate Ⅱ Mini instantly.

### 5.2.3 Remote Control

Sub-Menu

- Instant Control

- Task Scheduler

- Extend Output Control

- Netmate Update

#### 5.2.3.1 Instant Control

This part is to set UPS control command for sending instant self-test, switch off, restart UPS and Beeper.

#### 5.2.3.2 Task Scheduler

This part is to display our task scheduler, including the Carry out time, Dictate item, and Carry out Frequency, Task Param and Operation.

Click the “Add” button, the system will pop out the following box. Users can set the Target Project, which includes UPS Self-test, Switch Off and Sleep item. Users can also set the execute frequency and execute time.

1. Target Project

A, UPS Self-Test Time

Set UPS timing self-test.

B, UPS Self-Test Till Battery Voltage Low

Choose whether UPS self-test till battery voltage low.

C, UPS Switch Off

Set UPS timing switch off automatically.

D, UPS Sleep

Set UPS timing switch off automatically, after fixed time the UPS will be restarted automatically.

2. Task Attribute

Execute Frequency

Set execute frequency of timing control task.

Execute Time

Set execute starting time of timing control task.

#### 5.2.3.3 485 Bus Device Output Control

#### This part needs to connect signal collecting module to show.

#### 5.2.3.4 Netmate Update

This part is used for product upgrade and update. System provides two ways: detect Netmate new version and upgrade and Refresh.

### 5.2.4 History Record

This part is to display history record, users can learn about the UPS information simply and intuitively.

Sub-Menu

- History Event Record

- History Data Maintenance

#### 5.2.4.1 History Event Record

This page is to display record of all events. Record includes the Date/Time of the event and the event description.

#### 5.2.4.2 History Data Maintenance

This part is to set Everyday Time for Sending Log Mail and record history data time interval. And it also provides the connection of downloading all history event record and all history record.

### 5.2.5 System Help

Sub-Menu

- System Help

- About Netmate

#### 5.2.5.1 System Help

This part is to display the relevant operation information about Netmate.

#### 5.2.5.2 About Netmate

This part is to display basic information of Netmate. It includes Hardware Version/Software Version/Product Serial Number/Remain Time. It also provides the contact way.

# Chapter 6 Common Problem Solutions

## 6.1 Forget the IP address, how to do?

If forgot the IP address of Netmate Ⅱ Mini, user can connect the one end of configuration cable to the serial port of the computer and connect the other end to the RS232 connecting cable, and then connect to the RS232 port of the Netmate Ⅱ Mini. At last, connect with the power line, and user will find the IP through the following operation:

- Open the Hyper Terminal: click open Menu→ Procedures→ Accessories→ Communication→ Hyper Terminal;

- Set name according to user’s demand;

- Choose a serial port according to the connecting situation between monitoring card or monitoring host and the RS232 port of computer;

- Configure the port;

(B) 9600,   (D) 8,   (P) no,   (S) 1,   (F) no

5)  Click the “OK” button, user will open the following Hyper Terminal page, the picture will display the IP address of the monitoring card.

## 6.2 Why the device can be PING, but user cannot open the webpage?

1. Restart the device;

2. Check whether the IP is conflicted with other IP;

If user still cannot open the webpage, please cut off the Netmate Ⅱ Mini, click Open Menu→ Running→ Input “cmd” →click the “Enter” key，enter the doc order interface, then input ***.***. *** (***. ***. *** is the device IP), check whether the IP is effective, if the IP is tested through, it means there is the same IP in the network, the IP is conflicted.

3. Whether enable HTTP item or the default port has been modified.

If the device has been restarted, and there is no conflicted IP in the network, then check whether enable HTTP item or the default port has been modified. The operation is as follows:

1) User can connect the one end of configuration cable to the serial port of the computer and connect the other end to the RS232 connecting cable, and then connect to the RS232 port of Netmate Ⅱ Mini. At last, connect with the power line;

2) Open the Hyper Terminal; click open Menu→ Procedures→ Accessories→ Communication→ Hyper Terminal;

3) Set a name according to user’s demand;

4) Choose a serial port according to the connecting situation between monitoring card or monitoring host and the RS232 port of computer;

- Configure the port;

(B) 9600,   (D) 8,   (P) no,   (S) 1,   (F) no

6)  Click the “OK” button, user will open the following Hyper Terminal page;

7) Input the user name after the “login”, system default user name is admin, click the “Enter” key, then the Hyper Terminal will display the “Password:” input the relevant password, the default password is admin. At last click the “Enter” key, the Hyper Terminal will display the main configuration menu of Netmate Ⅱ Mini, the page is as follows:

8) Input 7 after the “please enter your choice:” user will enter the system function configuration menu of Netmate Ⅱ Mini; user can check and modify the function configuration. The page is as follows:

9) If the Http is disabled, user can modify the enable status via inputting 4 after the “Please enter your choice:” the operation is as follows:

10) If the HTTP default port has been modified, user can modify it via inputting 6 after “Please enter your choice:” operation is as follows:

11) Input 0 after “Please enter your choice:” after finishing the modification, exit Net configuration, and enter the main configuration menu. The operation is as follows:

12) Inputting 0 after “Please enter your choice:”, and the Hyper Terminal will display 3 ways to save and reboot for Netmate Ⅱ Mini, user can choose one way according to own real situation, the operation is as follows:

## 6.3 What is the login user name and password?

When login the Netmate Ⅱ Mini at first time via IE browser, user name is admin and password is also admin. But if login the webpage, user can set other user name, so other setting users can also login the webpage.

## 6.4 Forget the login password, how to do?

Please remember the login password of Netmate Ⅱ Mini, if the user forgot the password, the user must send the device back to our company to deal with it.

## 6.5 Cannot connect with the device, how to do?

Netmate Ⅱ Mini connection is normal according to PING order, UPS communication indicator is flashing, IP Power monitoring device displays the UPS is offline. Solution is as follows:

- Check the protocol configuration and Baud rate configuration;

Enter the system configuration page of Netmate Ⅱ Mini, check whether the protocol configuration and Baud rate configuration is right.

- Check the line order of conversion line;

If the settings of the protocol and baud rate are all right, please check whether the line order of conversion line is normal.

- Check the UPS;

If the protocol, Baud rate and line order of conversion line are all normal, please check whether the UPS is normal.

# Chapter 7 Notice Items

1. After finishing the configuration of Netmate Ⅱ Mini, user should cut off the power of the monitoring card first, and then plug out the relevant port configuration cable, void to damage the port of computer and monitoring card for the hot plug in and pull out.

2. The white cable in the package is used for the configuration of SNMP card; it cannot be used to connect UPS. In order to guarantee the UPS communication quality, please use the cable which is provided by UPS manufacturer.

# Text boxes

Http port number（default is 80）

Http Enable status