Front Panel Description And Operations

LED Description

The Charging LED GREEN indicates that the battery charger in the Extended Battery Pack is charging normally with the AC power cord attached to the Battery pack.

The Battery Test LED GREEN indicates that the DC output of the Extended Battery Pack (EBP) is normal. To perform the Battery Test,

- switch the breaker on the rear of the EBP to ON position

- press the Battery Test Button on the front panel of the EBP

- the DC output from the EBP is normal when the Battery Test LED is illuminated

Prior to connecting EBP’s, test each EBP to assure proper operation.

Rear Panel Description

1KVA  Battery pack rear panel

2KVA/3KVA Battery pack rear panel silkscreen

1. The DC Circuit Breaker connects and disconnects the DC bus voltage from the Battery pack to the UPS. The DC Circuit Breaker will disconnect/engage in the event of an over-current condition.

- The External Battery connector is for Daisy Chaining additional Battery Packs and/or connecting to the UPS.

- The AC Inlet is for connecting the input power cord to operate the Charger.

- The Input AC Breaker will disconnect/engage in the event that the Internal Charger draws excessive current.

- The External Battery cable is for connecting the Battery Pack to the UPS or Daisy Chaining additional Battery Packs.

Extended Battery Pack Operation

- The DC Circuit Breaker on the rear of the EBP connects and disconnects the DC bus voltage from the EBP to the UPS. The DC Circuit Breaker will also trip to the OFF position in the event of an over-current condition in the EBP.

1KVA  REAR VIEW

- The EBP’s use a cable shipped with each EBP to “daisy chain” together additional EBP’s to the first EBP being connected to the UPS in the appropriately labeled connector, or for connecting the first EBP to the UPS.

- The input AC Circuit Breaker will trip to the OFF position in the event that the internal EBP charger draws excessive current.

System Specifications

|  | EXTENDED BATTERY PACK MODELS | 1KVA | 2KVA | 3KVA |
| --- | --- | --- | --- | --- |
| INPUT | Voltage | 220 VAC |
|  | AC Current | 0.5A | 1A | 1.5A |
|  | Frequency | 50/60 Hz auto sensing |
|  | Input Protection | resettable circuit breaker |
| CHARGER OUTPUT | DC Voltage | 27.5 ±0.5V | 55.0 ±0.5V | 82.5 ±0.5V |
|  | DC Current | 2.0A |
|  | Output Protection | Fuse |
| BATTERY | Battery Type | sealed, non-spillable, maintenance free, valve regulated, lead acid |
|  | Extended Battery Packs | 1KVA | 2KVA | 3KVA |
|  | Battery Type (EBP) | 2 strings of (2) 12V 9 AH / 24V | 2 strings of (4) 12V 9AH / 48V | 2 strings of (6) 12V 9 AH / 72V |
|  | Recharge Time | 6 hours to 90% |
| PHYSICAL | Dimensions | W x D x H (inches) |
|  | Unit Dimensions | 17.3" x 15.0" x 3.4" | 17.3" x 20.5" x 5.2" | 17.3" x 20.5" x 5.2" |
|  | Shipping Dimensions | 23.9" x 20.2" x 6.7" | 25.7" x 23.9" x 8.3" | 25.7" x 23.9" x 8.3" |
|  | Unit Weight | 29.8 lbs | 51.4 lbs | 61.3 lbs |
|  | Shipping Weight | 32.0 lbs | 53.6 lbs | 63.5 lbs |
|  | Line Cord |  |
|  | Included in box | EBP, User Manual, DC cable, AC input cord |
|  | EXTENDED BATTERY PACK MODELS | 1KVA | 2KVA | 3KVA |
| WARRANTY | Warranty | Three years electronics / One year batteries |
| APPROVALS | North America |  |
| INDICATORS & ALARMS | LED Visual Display | Charging LED, Battery test LED |